## Sheet1
LUCKY ONE MALL
DETAIL OF ACCESS CONTROL SYSTEM
Floor | Zone | S.No | Location | Device S.No | IP Address | Pad Lock | Magnetic Plate | Bio Reader | Slave Reader | Power Supply with Box | Connection | Testing | Cat-6 Net wire | AC Power 220V | Remarks
Basement-2 | 1 | 1 | Electrical Room | AFHG04387 online | 10.10.20.102 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 2 | 2 | Electrical Room | AFHG02571 online | 10.10.20.100 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 3 | Communication Room | AFHG04381 fiber down | 10.10.20.101 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Communication Issue .Fiber Down
| 3 | 4 | Electrical Room | AFHG04386 | 10.10.20.103 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 5 | Communication Room | AFHG04129 | 10.10.20.104 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 6 | BTS Room | AFHG02580 | 10.10.20.105 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Communication Issue .Fiber Down
| 4 | 7 | Electrical Room | AFHG02578 communication issue | 10.10.20.106 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 8 | Communication Room | AFHG02579 communication issue | 10.10.20.107 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 9 | Guard Room |  | 10.10.20.108 | [9 empty] | Keys Not Available
|  | 10 | Lucky One Store | AFHG02574 | 10.10.20.109 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Keys Not Available
Basement-1 | 1 | 11 | ELectrical Room (Mr. Abbas) | AFHG04122 | 10.10.20.90 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 2 | 12 | Communication Room | AFHG04383 | 10.10.20.92 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 13 | SOK Room Entrance | AFHG04263 | 10.10.20.94 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Off Line ,Communication Issue
|  | 14 | Security Room | AFHG04268 | 10.10.20.95 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 15 | Brigadier Room | AFHG04267 | 10.10.20.96 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 16 | Security to SOK Room Entrance | AFHG02629 | 10.10.20.97 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 17 | LV Room | device not installed | 10.10.20.111 | OK | OK | OK | OK | OK | OK | OK | OK | Not Provided By Lucky one | Power Not Provided
| 3 | 18 | Communication Room | AFHG04382 | 10.10.20.99 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 19 | LV Room | connector done Power Not connected | 10.10.20.112 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Ethernet not Connected to Switch
|  | 20 | MV Room | connector done | 10.10.20.113 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 21 | Engineering Room |  | 10.10.20.114 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 22 | BTS Room | locked | 10.10.20.115 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Communication Issue .Fiber Down
| 4 | 23 | Communication Room | AFHG04129 | 10.10.20.91 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Connector issue
|  | 24 | LV Room |  | 10.10.20.116 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 25 | MV Room |  | 10.10.20.117 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 26 | Record Room |  | 10.10.20.118 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Ethernet not Connected to Switch
|  | 27 | Guard Room | AFHG04121 | 10.10.20.93 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 28 | Lucky One Store | AFHG04126 | 10.10.20.98 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
Lower Ground | 1 | 29 | AHU Room | AFHG04266 | 10.10.20.57 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 2 | 30 | Electrical & Communication Room | AFHG04265 | 10.10.20.55 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 31 | AHU Room | AFHG04262 | 10.10.20.56 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 3 | 32 | AHU Room | AFHG04264 | 10.10.20.51 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 33 | BTS Room | AFHG04270 | 10.10.20.52 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 34 | Electrical Room | AFHG04261 | 10.10.20.53 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 35 | Communication Room | AFHG04269 | 10.10.20.54 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 4 | 36 | Electrical & Communication Room | AFHG02624 | 10.10.20.58 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 37 | AHU Room | AFHG02626 | 10.10.20.59 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 38 | Data Room Entrance | AFHG02625 | 10.10.20.60 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 39 | Data Office Entrance | AFHG02340 | 10.10.20.61 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 40 | Server Room | AFHG03542 | 10.10.20.62 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
Ground Floor | 1 | 41 | AHU Room | AFHG04388 | 10.10.20.69 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 2 | 42 | Electrical & Communication Room | AFHG02623 | 10.10.20.67 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 43 | AHU Room | AFHG04470 | 10.10.20.68 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 3 | 44 | AHU Room | AFHG04469 | 10.10.20.63 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 45 | BTS Room | AFHG02332 | 10.10.20.64 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 46 | Electrical Room | AFHG02639 | 10.10.20.65 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 47 | Communication Room | AFHG02333 | 10.10.20.66 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 4 | 48 | Electrical & Communication Room | AFHG02637 | 10.10.20.70 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 49 | AHU Room | AFHG02826 | 10.10.20.71 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
First Floor | 1 | 50 | AHU Room | AFHG02638 | 10.10.20.78 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 2 | 51 | Electrical & Communication Room | AFHG04021 | 10.10.20.76 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 52 | AHU Room | AFHG04024 | 10.10.20.77 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 3 | 53 | AHU Room | AFHG04385 | 10.10.20.72 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 54 | BTS Room | AFHG04028 | 10.10.20.73 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 55 | Electrical Room | AFHG04023 | 10.10.20.74 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 56 | Communication Room | AFHG04393 | 10.10.20.75 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 4 | 57 | Electrical & Communication Room | AFHG04025 | 10.10.20.79 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 58 | AHU Room | AFHG04022 | 10.10.20.80 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
Second Floor | 1 | 59 | AHU Room | AFHG04389 | 10.10.20.87 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 60 | Onderland Electrical Room | AFHG04384 | 10.10.20.110 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Communication Issue
| 2 | 61 | Electrical & Communication Room | AFHG04029 | 10.10.20.85 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 62 | AHU Room | AFHG04123 | 10.10.20.86 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 63 | IT Office entrance | AFHG02575 | 10.10.31.17 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online,
| 3 | 64 | AHU Room | AFHG04027 | 10.10.20.81 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 65 | BTS Room | AFHG04026 | 10.10.20.82 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 66 | Electrical Room | AFHG04030 | 10.10.20.83 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 67 | Communication Room | AFHG04127 | 10.10.20.84 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
| 4 | 68 | Electrical & Communication Room | AFHG04128 | 10.10.20.88 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online
|  | 69 | AHU Room | AFHG04390 | 10.10.20.89 | OK | OK | OK | OK | OK | OK | OK | OK | OK | Online

## GPIO Enterences
Floor | Zone | S.No | Entrance/ Exit | Door Type | Door Contact | GPIO Module Installed Location | GPIO Module | IP Address | Power | Cat-6 wire | Cat-6 Connector | Switch Connectivity | Port Open/Closed | Remarks
Basement-2 | 2 | 1 | Exit Center | Fixed | Not Install | On Door Near Celling Opening | [7 empty] | Celling Access Panel/ Opening Required
|  | 2 | Exit Corner | Fixed | Not Install | On Door Near Celling Opening | [7 empty] | Celling Access Panel/ Opening Required
|  | 3 | Food Court Entrance | Fixed | 2 | On Door Near Celling Opening
|  | 4 | Food Court Exit | Fixed | 1 | On Door Near Celling Opening
| 3 | 5 | Entrance Outside | Siliding | Not Required | Com. 1
|  | 6 | Entrance Inside | Siliding | Not Required | Com. 1
|  | 7 | Exit Inside | Siliding | Not Required | Com. 1
|  | 8 | Exit Outside | Siliding | Not Required | Com. 1
|  | 9 | Emergency Exit Lobby | Fixed | Not Install | On Door Near Celling Opening | [7 empty] | will be install on Friday
|  | 10 | Entrance Center | Fixed | 2 | On Door Near Celling Opening
|  | 11 | Entrance Corner | Fixed | 1 | On Door Near Celling Opening
| 4 | 12 | Entrance Outside | Siliding | Not Required | Com. 3
|  | 13 | Entrance Inside | Siliding | Not Required | Com. 3
|  | 14 | Exit Inside | Siliding | Not Required | Com. 3
|  | 15 | Exit Outside | Siliding | Not Required | Com. 3
Basement-1 | 2 | 16 | Exit Center | Fixed | 2 | On Door Near Celling Opening
|  | 17 | Exit Corner | Fixed | 1 | On Door Near Celling Opening
|  | 18 | Food Court Entrance | Fixed | 2 | On Door Near Celling Opening
|  | 19 | Food Court Exit | Fixed | 1 | On Door Near Celling Opening
| 3 | 20 | Entrance Outside | Siliding | Not Required | Com. 1
|  | 21 | Entrance Inside | Siliding | Not Required | Com. 1
|  | 22 | Exit Inside | Siliding | Not Required | Com. 1
|  | 23 | Exit Outside | Siliding | Not Required | Com. 1
|  | 24 | Entrance Center | Fixed | 2 | On Door Near Celling Opening
|  | 25 | Entrance Corner | Fixed | 1 | On Door Near Celling Opening
| 4 | 26 | Entrance Outside | Siliding | Not Required | Com. 3
|  | 27 | Entrance Inside | Siliding | Not Required | Com. 3
|  | 28 | Exit Inside | Siliding | Not Required | Com. 3
|  | 29 | Exit Outside | Siliding | Not Required | Com. 3
LOWER Ground Floor | 1 | 30 | Main Entrance Outside Center | Siliding | Not Required | On Door Near Celling Opening
|  | 31 | Main Entrance Inside Center | Siliding | Not Required | On Door Near Celling Opening
|  | 32 | Exit Left Side Outside | Siliding | Not Required | On Door Near Celling Opening
|  | 33 | Exit Left Side Inside | Siliding | Not Required | On Door Near Celling Opening
|  | 34 | Exit Right Side Outside | Siliding | Not Required | On Door Near Celling Opening
|  | 35 | Exit Left Side Inside | Siliding | Not Required | On Door Near Celling Opening
Ground Floor | 1 | 36 | Main Entrance Outside Center | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
|  | 37 | Main Entrance Inside Center | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
|  | 38 | Exit Left Side Outside | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
|  | 39 | Exit Left Side Inside | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
|  | 40 | Exit Right Side Outside | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
|  | 41 | Exit Left Side Inside | Siliding | Not Required | On LG Main Entrance Door Near Celling Opening
| 4 | 42 | Food Court Entrance 1 Outside Center Door | Siliding | Not Required | Com. 03 | Install |  | OK
|  | 43 | Food Court Entrance 1 Inside Center Door | Siliding | Not Required | Com. 03 | Install |  | OK
|  | 44 | Food Court Entrance 1 Outside Left Door | Fixed | 2 | Com. 03 | Install |  | OK
|  | 45 | Food Court Entrance 1 Inside Left Door | Fixed | 2 | Com. 03 | Install |  | OK
|  | 46 | Food Court Entrance 1 Outside Right Door | Fixed | 2 | Com. 03 | Install |  | OK
|  | 47 | Food Court Entrance 1 Inside Right Door | Fixed | 2 | Com. 03 | Install |  | OK
Ground Floor | 3 | 48 | Food Court Entrance 2 Outside Center Door | Siliding | Not Required | Com. 03
|  | 49 | Food Court Entrance 2 Inside Center Door | Siliding | Not Required | Com. 03
|  | 50 | Food Court Entrance 2 Outside Left Door | Fixed | 2 | Com. 03
|  | 51 | Food Court Entrance 2 Inside Left Door | Fixed | 2 | Com. 03
|  | 52 | Food Court Entrance 2 Outside Right Door | Fixed | 2 | Com. 03
|  | 53 | Food Court Entrance 2 Inside Right Door | Fixed | 2 | Com. 03
| 2 | 54 | Food Court Entrance 3 Outside Center Door | Siliding | Not Required | Com. 03
|  | 55 | Food Court Entrance 3 Inside Center Door | Siliding | Not Required | Com. 03
|  | 56 | Food Court Entrance 3 Outside Left Door | Fixed | 1 | Com. 03
|  | 57 | Food Court Entrance 3 Inside Left Door | Fixed | 1 | Com. 03
|  | 58 | Food Court Entrance 3 Outside Right Door | Fixed | 1 | Com. 03
|  | 59 | Food Court Entrance 3 Inside Right Door | Fixed | 1 | Com. 03

## Emergency Stairs
Emergency Stair No | Zone | Near By | Floor | S. No | Door Type | Door Contact | GPIO Module Installed Location | GPIO Module | IP Address | Power | Cat-6 wire | Cat-6 Connector | Switch Connectivity | Port Open/ Closed | Remarks
Stair No. 01 | 1 | Masjid | B2 | 1 | Fixed |  | On Door
|  |  | B1 | 2 | Fixed |  | On Door
|  |  | LG | 3 | Fixed |  | On Door
|  |  | Ground | 4 | Fixed |  | On Door
|  |  | First | 5 | Fixed |  | On Door
|  |  | Second | 6 | Fixed |  | On Door
|  |  | Third | 7 | Fixed |  | On Door
Stair No. 02 | 1 | Hyper Star | B2 | 8 | Fixed |  | On Door
|  |  | B1 | 9 | Fixed |  | On Door
|  |  | LG | 10 | Fixed |  | On Door
|  |  | Ground | 11 | Fixed |  | On Door
|  |  | First | 12 | Fixed |  | On Door
|  |  | Second | 13 | Fixed |  | On Door
|  |  | Third | 14 | Fixed |  | On Door
Stair No. 03 | 1 | Time office | B2 | 15 | Fixed |  | On Door
|  |  | B1 | 16 | Fixed |  | On Door
|  |  | LG | 17 | Fixed |  | On Door
|  |  | Ground | 18 | Fixed |  | On Door
|  |  | First | 19 | Fixed |  | On Door
|  |  | Second | 20 | Fixed |  | On Door
|  |  | Third | 21 | Fixed |  | On Door
Stair No. 04 | 2 | Comm. 02 | B2 | 22 | Fixed |  | On Door
|  |  | B1 | 23 | Fixed |  | On Door
|  |  | LG | 24 | Fixed |  | On Door
|  |  | Ground | 25 | Fixed |  | On Door
|  |  | First | 26 | Fixed |  | On Door
|  |  | Second | 27 | Fixed |  | On Door
|  |  | Third | 28 | Fixed |  | On Door
Stair No. 05 | 2 | Back Side Hyper Star | B2 | 29 | Fixed |  | On Door
|  |  | B1 | 30 | Fixed |  | On Door
|  |  | LG | 31 | Fixed |  | On Door
|  |  | Ground | 32 | Fixed |  | On Door
|  |  | First | 33 | Fixed |  | On Door
|  |  | Second | 34 | Fixed |  | On Door
|  |  | Third | 35 | Fixed |  | On Door
Stair No. 06 | 2 | Food Court Outside Mall Back Side | B2 | 36 | Fixed |  | On Door
|  |  | B1 | 37 | Fixed |  | On Door
|  |  | LG | 38 | Fixed |  | On Door
|  |  | Ground | 39 | Fixed |  | On Door
|  |  | First | 40 | Fixed |  | On Door
|  |  | Second | 41 | Fixed |  | On Door
|  |  | Third | 42 | Fixed |  | On Door
Stair No. 07 | 3 | Comm. 01 | B2 | 43 | Fixed |  | On Door
|  |  | B1 | 44 | Fixed |  | On Door
|  |  | LG | 45 | Fixed |  | On Door
|  |  | Ground | 46 | Fixed |  | On Door
|  |  | First | 47 | Fixed |  | On Door
|  |  | Second | 48 | Fixed |  | On Door
|  |  | Third | 49 | Fixed |  | On Door
Stair No. 08 | 4 | Comm. 03 | B2 | 50 | Fixed |  | On Door
|  |  | B1 | 51 | Fixed |  | On Door
|  |  | LG | 52 | Fixed |  | On Door
|  |  | Ground | 53 | Fixed |  | On Door
|  |  | First | 54 | Fixed |  | On Door
|  |  | Second | 55 | Fixed |  | On Door
|  |  | Third | 56 | Fixed |  | On Door